## Sheet1
[6 empty] | Page 1 | of | 2
Loup Power District
SWITCHING ORDER RECORD
SWITCHING ORDER/HOLD ORDER NO.: |  |  | 10-002 | TIME: |  | DATE:
TO REMOVE FROM SERVICE: |  | Breaker No. 302 |  | LOCATION: | Creston 115kv substation
SWITCHMAN: |  |  |  | DISPATCHER:
SWITCHING ORDER/HOLD ORDER NO.: |  |  | 10-002 | TIME: |  | DATE:
TO RETURN FROM SERVICE: |  | Breaker No. 302 |  | LOCATION: | Creston 115kv substation
SWITCHMAN: |  |  |  | DISPATCHER:
TIME EXECUTED
ORDER: | This switching order is to clear breaker 302 at Creston for maintenance.
1.Close loadbreak switch No. 999 outside of Creston substation.
2.System Control Doniphan: Place recloser cutout switch for breaker No. 302 at Creston to Off position by
supervisory.
3.System Control Doniphan: Open and Tag breaker No. 302 at Creston by supervisory.
4.LPPD Dispatch: Tag Creston breaker No. 302 control point on SCADA.
5.At Creston: Confirm recloser cutout switch for breaker No. 302 on front of panel No. 2 in Off position.
6.Confirm Open breaker No. 302.
7.Place supervisory Local/Remote switch on front of panel No. 2 for breaker No. 302 to Local position and Tag.
8.Open and Tag disconnects No. 302-D (2 sets).
9.Confirm Open and Tag bypass switch No. 301.
10.Clearance order No. 10-007 issued to at
On breaker No. 302 between Open and Tagged disconnects No. 302-D (2 sets), and Open and Tagged bypass
switch No. 301.
TO RETURN TO NORMAL
11.Clearance order No. 10-007 released by at
12.Confirm Open breaker No. 302.
13.Remove Tag and leave Open bypass switch No. 301.
14.Remove Tags and Close disconnects No. 302-D (2 sets).
15.Remove Tag and place supervisory Local/Remote switch on front of panel No. 2 for breaker No. 302 to
Remote position.
[6 empty] | Page 2 | of | 2
Loup Power District
SWITCHING ORDER RECORD
SWITCHING ORDER/HOLD ORDER NO.: |  |  |  | TIME: |  | DATE:
TO REMOVE FROM SERVICE: |  |  |  | LOCATION:
SWITCHMAN: |  |  |  | DISPATCHER:
SWITCHING ORDER/HOLD ORDER NO.: |  |  | 10-002 | TIME: |  | DATE:
TO RETURN FROM SERVICE: |  | Breaker No. 302 |  | LOCATION: | Creston 115kv substation
SWITCHMAN: |  |  |  | DISPATCHER:
TIME EXECUTED
ORDER:
16.LPPD Dispatch: Remove Tag from Creston breaker No. 302 control point on SCADA.
17.System Control Doniphan: Remove Tag and Close breaker No. 302 at Creston by supervisory.
18.System Control Doniphan: Place recloser cutout switch for breaker No. 302 at Creston to On position by
supervisory.
Proceed to switching to clear breaker 304.
[6 empty] | Page 3 | of | 2
Loup Power District
SWITCHING ORDER RECORD
SWITCHING ORDER/HOLD ORDER NO.: |  |  |  | TIME: |  | DATE:
TO REMOVE FROM SERVICE: |  |  |  | LOCATION:
SWITCHMAN: |  |  |  | DISPATCHER:
SWITCHING ORDER/HOLD ORDER NO.: |  |  |  | TIME: |  | DATE:
TO RETURN FROM SERVICE: |  |  |  | LOCATION:
SWITCHMAN: |  |  |  | DISPATCHER:
TIME EXECUTED
ORDER:
[6 empty] | Page 4 | of | 2
Loup Power District
SWITCHING ORDER RECORD
SWITCHING ORDER/HOLD ORDER NO.: |  |  |  | TIME: |  | DATE:
TO REMOVE FROM SERVICE: |  |  |  | LOCATION:
SWITCHMAN: |  |  |  | DISPATCHER:
SWITCHING ORDER/HOLD ORDER NO.: |  |  |  | TIME: |  | DATE:
TO RETURN FROM SERVICE: |  |  |  | LOCATION:
SWITCHMAN: |  |  |  | DISPATCHER:
TIME EXECUTED
ORDER: